## English
PUMP SIZING CALCULATION
CheGuide.com | [8 empty] | Tag No. |  | P-101 |  |  |  |  | Suction Calculations |  |  |  | Outlet Calculations |  |  |  |  | Head Equation (2nd Order Curve Fitting)
Chemical Engineer's Guide | [8 empty] | Description |  | Feed Pump | [13 empty] | -0.0019957 | -0.10066 | 149.9348
[9 empty] | Date |  | 06-May-2017 |  |  |  |  | Selected ID |  | 6 |  | Selected ID |  | 6 |  |  | 8.9021e-06 | 0.0019848 | 0.083448
User Input | [8 empty] | By |  | CheGuide |  |  |  |  | Selected Schedule |  | 7 |  | Selected Schedule |  | 7 |  |  | 1 | 0.10519 | #N/A
[16 empty] | Pipe ID Selected |  | 3.068 | inch | Pipe ID Selected |  | 3.068 | inch
[18 empty] | 3.068 | inch |  |  | 3.068 | inch |  | Efficiency Equation (2nd Order Curve Fitting)
[16 empty] | Area |  | 0.051338 | ft2 | Area |  | 0.051338 | ft2 |  | -0.0017458 | 0.42345 | 20.1368
Flowrate |  |  | 100 | US gpm | [11 empty] | Velocity |  | 4.3399 | ft/s | Velocity |  | 4.3399 | ft/s |  | 1.5633e-05 | 0.0034856 | 0.14655
Density |  |  | 62.4 | lb/ft3 | [11 empty] | Re |  | 103035.8491 |  | Re |  | 103035.8491 |  |  | 0.99955 | 0.18473 | #N/A
Viscosity |  |  | 1 | cP | [11 empty] | e/D |  | 0.0005867 |  | e/D |  | 0.0005867
Vapor Pressure |  |  | 15 | psia | [11 empty] | A |  | 4.9554e+20 |  | A |  | 4.9554e+20 |  |  | System Curve (2nd Order Curve Fitting)
[16 empty] | B |  | 9.5994e-08 |  | B |  | 9.5994e-08 |  |  | 0.0011033 | 0.013867 | 100.7739
Differential DP |  |  | 49.0084 | psi | [11 empty] | f |  | 0.020711 |  | f |  | 0.020711 |  |  | 2.3589e-06 | 0.0004398 | 0.017082
Differential Head |  |  | 113.2094 | ft | [11 empty] | DP1 |  | 1.0267 | psi/100ft | DP |  | 1.0267 | psi/100ft |  | 1 | 0.028618 | #N/A
Hydraulic power |  |  | 2.8588 | bhp | [11 empty] | Pressure |  | 20.5718 | psi | Pressure |  | 69.5802
NPSH available |  |  | 12.8709 | ft | [20 empty] | Solution of System & Head Curve | [5 empty] | Efficiency | 45.5429 | %
[25 empty] | -0.003099 | -0.11453 | 49.1609
Suction Condition | [7 empty] | Discharge Condition | [7 empty] | Curve Fitting |  |  |  |  | Maximum Flow |  | 180
Pressure |  | P1 | 25 | psia |  |  |  | Pressure |  | P2 | 50 | psia | [8 empty] | Division |  | 20 |  | Determinant |  | 0.62251 | TRUE | 0.78899 |  |  | X | Y
Static Head |  | h1 | 5 | ft |  |  |  | Static Head |  | h2 | 25 | ft |  |  |  | Flow | Head | Efficiency |  |  | Increment |  | 9 |  | Roots |  | -145.777 | 108.8206 |  |  |  | 108.8206 | 0
Equipment DP |  |  | 5 | psi |  |  |  | Equipment DP |  |  | 5 | psi |  |  | 1 | 0 | 150 | 20 | [6 empty] | Selected Flow |  | 108.8206 | GPM | Head | 115.3477 | ft | 108.8206 | 115.3477
Misc DP |  |  | 0 | psi |  |  |  | Misc DP |  |  | 0 | psi |  |  | 2 | 20 | 147 | 28 |  |  |  | Suction Pipe
[15 empty] | 3 | 50 | 140 | 37 |  |  | Flow | Velocity | Reynold | A | B | f | DP1 | Elb, 90LR | Elb, 45LR | Tees, Thru | Tees, Bran | Ball | Butterfly | Gate | Globe | Check | Plug | Pipe | Sum K | DP | Suct P | Diff P | System Curve | Pump Head | Efficiency %
Piping | [7 empty] | Piping | [6 empty] | 4 | 80 | 129 | 43 |  |  | GPM | ft/s | [5 empty] | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | [6 empty] | %
Length |  | L1 | 120 | ft |  |  |  | Length |  | L2 | 300 | ft |  |  | 5 | 100 | 120 | 45 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.1645 | 43.658 | 100.85 | 149.9348 | 20.1368
Pipe Diameter |  |  | 3 | inch |  |  |  | Pipe Diameter |  |  | 3 | inch |  |  | 6 | 150 | 90 | 44 |  | 2 | 9 | 0.39059 | 9273.2264 | 1.3052e+19 | 5180398960.7026 | 0.032631 | 0.013102 | 0.35146 | 0.25281 | 0.67915 | 1.147 | 0.25281 | 0.41776 | 0.16495 | 5.4655 | 2.1507 | 0.43932 | 0.51725 | 3.1126 | 0.0031947 | 22.1456 | 43.7221 | 100.9981 | 148.8672 | 23.8064
Sch/ Thick |  |  | 40 |  |  |  |  | Sch/ Thick |  |  | 40 |  |  |  | 7 | 180 | 67 | 40 |  | 3 | 18 | 0.78118 | 18546.4528 | 4.8691e+19 | 79046.615 | 0.02768 | 0.044455 | 0.30832 | 0.22585 | 0.67106 | 1.1039 | 0.22585 | 0.37462 | 0.14877 | 5.3847 | 2.0698 | 0.3854 | 0.50863 | 2.9665 | 0.012179 | 22.099 | 43.8796 | 101.3619 | 147.4763 | 27.1932
Pipe ID |  | ID1 | 3.068 | inch |  |  |  | Pipe ID |  | ID2 | 3.068 | inch |  |  | 8 | 200 | 50 | 35 |  | 4 | 27 | 1.1718 | 27819.6793 | 9.5328e+19 | 120.3436 | 0.02545 | 0.091968 | 0.29395 | 0.21686 | 0.66836 | 1.0895 | 0.21686 | 0.36024 | 0.14338 | 5.3577 | 2.0428 | 0.36743 | 0.50575 | 2.9178 | 0.026952 | 22.0272 | 44.1216 | 101.9209 | 145.7621 | 30.2972
[15 empty] | 9 | 200 | 50 | 35 |  | 5 | 36 | 1.5624 | 37092.9057 | 1.4673e+20 | 1.2062 | 0.024114 | 0.15492 | 0.28676 | 0.21237 | 0.66702 | 1.0823 | 0.21237 | 0.35305 | 0.14068 | 5.3442 | 2.0294 | 0.35845 | 0.50431 | 2.8935 | 0.047515 | 21.9311 | 44.4452 | 102.6683 | 143.7246 | 33.1183
Roughness |  |  | 0.0018 | inch |  |  |  | Roughness |  |  | 0.0018 | inch |  |  | 10 | 200 | 50 | 35 |  | 6 | 45 | 1.953 | 46366.1321 | 1.9965e+20 | 0.03395 | 0.023204 | 0.23292 | 0.28244 | 0.20968 | 0.66621 | 1.078 | 0.20968 | 0.34874 | 0.13906 | 5.3361 | 2.0213 | 0.35305 | 0.50345 | 2.8789 | 0.073868 | 21.8111 | 44.8486 | 103.6003 | 141.3637 | 35.6567
[20 empty] | 7 | 54 | 2.3435 | 55639.3585 | 2.5233e+20 | 0.0018363 | 0.022534 | 0.32573 | 0.27957 | 0.20788 | 0.66567 | 1.0751 | 0.20788 | 0.34586 | 0.13799 | 5.3307 | 2.0159 | 0.34946 | 0.50288 | 2.8691 | 0.10601 | 21.6676 | 45.3309 | 104.7144 | 138.6796 | 37.9122
Fittings |  |  | No. | K | DP |  |  | Fittings |  |  | No. | K | DP | [6 empty] | 8 | 63 | 2.7341 | 64912.5849 | 3.0381e+20 | 0.00015588 | 0.022017 | 0.43318 | 0.27751 | 0.20659 | 0.66528 | 1.0731 | 0.20659 | 0.34381 | 0.13722 | 5.3269 | 2.012 | 0.34689 | 0.50246 | 2.8622 | 0.14394 | 21.5007 | 45.8914 | 106.0092 | 135.6722 | 39.8849
Elbows, 90LR |  |  | 1 | 0.27295 | 0.034586 |  |  | Elbows, 90LR |  |  | 1 | 0.27295 | 0.034586 | [6 empty] | 9 | 72 | 3.1247 | 74185.8114 | 3.5359e+20 | 1.8404e-05 | 0.021604 | 0.55515 | 0.27597 | 0.20563 | 0.66499 | 1.0715 | 0.20563 | 0.34227 | 0.13664 | 5.324 | 2.0091 | 0.34497 | 0.50216 | 2.8569 | 0.18766 | 21.3107 | 46.5296 | 107.4835 | 132.3414 | 41.5748
Elbows, 45LR |  |  | 1 | 0.20374 | 0.025816 |  |  | Elbows, 45LR |  |  | 1 | 0.20374 | 0.025816 | [6 empty] | 10 | 81 | 3.5153 | 83459.0378 | 4.0141e+20 | 2.7957e-06 | 0.021264 | 0.69156 | 0.27477 | 0.20488 | 0.66477 | 1.0703 | 0.20488 | 0.34107 | 0.13619 | 5.3218 | 2.0069 | 0.34347 | 0.50192 | 2.8529 | 0.23717 | 21.0975 | 47.2452 | 109.1363 | 128.6874 | 42.9818
Tees, Thru |  |  | 1 | 0.66443 | 0.08419 |  |  | Tees, Thru |  |  | 1 | 0.66443 | 0.08419 | [6 empty] | 11 | 90 | 3.9059 | 92732.2642 | 4.4715e+20 | 5.1804e-07 | 0.020979 | 0.84234 | 0.27382 | 0.20428 | 0.66459 | 1.0694 | 0.20428 | 0.34011 | 0.13583 | 5.32 | 2.0051 | 0.34227 | 0.50173 | 2.8496 | 0.29247 | 20.8612 | 48.0377 | 110.9671 | 124.71 | 44.1061
Tees, Branch |  |  | 1 | 1.0685 | 0.13539 |  |  | Tees, Branch |  |  | 1 | 1.0685 | 0.13539 | [6 empty] | 12 | 99 | 4.2965 | 102005.4906 | 4.9082e+20 | 1.1274e-07 | 0.020736 | 1.0074 | 0.27303 | 0.20379 | 0.66444 | 1.0686 | 0.20379 | 0.33933 | 0.13554 | 5.3185 | 2.0036 | 0.34129 | 0.50157 | 2.847 | 0.35356 | 20.602 | 48.9071 | 112.9753 | 120.4094 | 44.9475
Ball Valves |  |  |  | 0.20374 |  |  |  | Ball Valves |  |  |  | 0.20374 | [7 empty] | 13 | 108 | 4.6871 | 111278.7171 | 5.3245e+20 | 2.802e-08 | 0.020526 | 1.1868 | 0.27238 | 0.20339 | 0.66432 | 1.0679 | 0.20339 | 0.33868 | 0.13529 | 5.3173 | 2.0024 | 0.34047 | 0.50144 | 2.8448 | 0.42044 | 20.3199 | 49.853 | 115.1605 | 115.7854 | 45.506
Butterfly Valves |  |  |  | 0.33925 |  |  |  | Butterfly Valves |  |  |  | 0.33925 | [7 empty] | 14 | 117 | 5.0777 | 120551.9435 | 5.7211e+20 | 7.7852e-09 | 0.020343 | 1.3804 | 0.27183 | 0.20304 | 0.66422 | 1.0674 | 0.20304 | 0.33812 | 0.13508 | 5.3162 | 2.0014 | 0.33978 | 0.50133 | 2.8429 | 0.49311 | 20.0149 | 50.8754 | 117.5223 | 110.8381 | 45.7818
Gate Valves |  |  | 1 | 0.13551 | 0.01717 |  |  | Gate Valves |  |  | 1 | 0.13551 | 0.01717 | [6 empty] | 15 | 126 | 5.4683 | 129825.1699 | 6.0989e+20 | 2.3786e-09 | 0.020181 | 1.5882 | 0.27135 | 0.20274 | 0.66413 | 1.0669 | 0.20274 | 0.33765 | 0.13491 | 5.3153 | 2.0005 | 0.33919 | 0.50123 | 2.8413 | 0.57157 | 19.6871 | 51.9742 | 120.0603 | 105.5675 | 45.7748
Globe Valves |  |  |  | 5.3183 |  |  |  | Globe Valves |  |  |  | 5.3183 | [7 empty] | 16 | 135 | 5.8589 | 139098.3963 | 6.4588e+20 | 7.8868e-10 | 0.020036 | 1.8101 | 0.27094 | 0.20249 | 0.66405 | 1.0665 | 0.20249 | 0.33724 | 0.13475 | 5.3146 | 1.9997 | 0.33868 | 0.50115 | 2.8399 | 0.65581 | 19.3365 | 53.1491 | 122.7745 | 99.9737 | 45.4849
Check Valves |  |  |  | 2.0035 |  |  |  | Check Valves |  |  | 1 | 2.0035 | 0.25386 | [6 empty] | 17 | 144 | 6.2494 | 148371.6227 | 6.8019e+20 | 2.8083e-10 | 0.019907 | 2.0462 | 0.27058 | 0.20226 | 0.66398 | 1.0661 | 0.20226 | 0.33688 | 0.13462 | 5.3139 | 1.999 | 0.33823 | 0.50108 | 2.8387 | 0.74585 | 18.9632 | 54.4002 | 125.6645 | 94.0565 | 44.9122
Plug Valves |  |  |  | 0.34119 |  |  |  | Plug Valves |  |  |  | 0.34119 | [7 empty] | 18 | 153 | 6.64 | 157644.8492 | 7.1291e+20 | 1.0646e-10 | 0.019791 | 2.2965 | 0.27026 | 0.20206 | 0.66392 | 1.0658 | 0.20206 | 0.33656 | 0.1345 | 5.3133 | 1.9984 | 0.33783 | 0.50101 | 2.8376 | 0.84167 | 18.567 | 55.7274 | 128.7302 | 87.816 | 44.0566
Pipe Entrance |  |  | 1 | 0.50155 | 0.063552 |  |  | Pipe Exit |  |  | 1 | 1 | 0.12671 | [6 empty] | 19 | 162 | 7.0306 | 166918.0756 | 7.4413e+20 | 4.2658e-11 | 0.019685 | 2.5608 | 0.26998 | 0.20189 | 0.66387 | 1.0655 | 0.20189 | 0.33628 | 0.13439 | 5.3128 | 1.9979 | 0.33748 | 0.50096 | 2.8366 | 0.94329 | 18.1482 | 57.1305 | 131.9714 | 81.2522 | 42.9183
[5 empty] | 0.36071 | [7 empty] | 0.67772 | [6 empty] | 20 | 171 | 7.4212 | 176191.302 | 7.7394e+20 | 1.796e-11 | 0.019589 | 2.8393 | 0.26973 | 0.20173 | 0.66382 | 1.0653 | 0.20173 | 0.33603 | 0.1343 | 5.3123 | 1.9974 | 0.33716 | 0.50091 | 2.8358 | 1.0507 | 17.7066 | 58.6095 | 135.388 | 74.365 | 41.4971
Velocity |  |  | 4.3399 | ft/s |  |  |  | Velocity |  |  | 4.3399 | ft/s | [7 empty] | 21 | 180 | 7.8118 | 185464.5284 | 8.0243e+20 | 7.9047e-12 | 0.0195 | 3.1319 | 0.2695 | 0.20159 | 0.66378 | 1.0651 | 0.20159 | 0.3358 | 0.13421 | 5.3119 | 1.997 | 0.33688 | 0.50086 | 2.835 | 1.1639 | 17.2424 | 60.1644 | 138.9798 | 67.1546 | 39.7931
Reynold's No. |  |  | 103035.8491 |  |  |  |  | Reynold's No. |  |  | 103035.8491
Pipe DP |  |  | 1.0267 | psi/100ft |  |  |  | Pipe DP |  |  | 1.0267 | psi/100ft | [9 empty] | Discharge Conditions
Suction Pressure |  |  | 20.5718 | psia |  |  |  | Discharge Pressure |  |  | 69.5802 | psia | [8 empty] | Flow | Velocity | Reynold | A | B | f | DP1 | Elb, 90LR | Elb, 45LR | Tees, Thru | Tees, Bran | Ball | Butterfly | Gate | Globe | Check | Plug | Pipe | Sum K | DP | Disch P
[21 empty] | GPM | ft/s | [5 empty] | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 1
[20 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 65.8225
| Pump Manufacturer's Curve | [6 empty] | Maximum Flow |  |  | 180 | US gpm | [7 empty] | 2 | 9 | 0.39059 | 9273.2264 | 1.3052e+19 | 5180398960.7026 | 0.032631 | 0.013102 | 0.35146 | 0.25281 | 0.67915 | 1.147 | 0.25281 | 0.41776 | 0.16495 | 5.4655 | 2.1507 | 0.43932 | 1 | 5.7461 | 0.0058975 | 65.8677
[8 empty] | Flow value till which System and Head Curve | [11 empty] | 3 | 18 | 0.78118 | 18546.4528 | 4.8691e+19 | 79046.615 | 0.02768 | 0.044455 | 0.30832 | 0.22585 | 0.67106 | 1.1039 | 0.22585 | 0.37462 | 0.14877 | 5.3847 | 2.0698 | 0.3854 | 1 | 5.5277 | 0.022693 | 65.9786
| Flow | Head | Efficiency |  |  |  |  | are calculated | [11 empty] | 4 | 27 | 1.1718 | 27819.6793 | 9.5328e+19 | 120.3436 | 0.02545 | 0.091968 | 0.29395 | 0.21686 | 0.66836 | 1.0895 | 0.21686 | 0.36024 | 0.14338 | 5.3577 | 2.0428 | 0.36743 | 1 | 5.4549 | 0.050388 | 66.1488
| gpm | ft | % | [16 empty] | 5 | 36 | 1.5624 | 37092.9057 | 1.4673e+20 | 1.2062 | 0.024114 | 0.15492 | 0.28676 | 0.21237 | 0.66702 | 1.0823 | 0.21237 | 0.35305 | 0.14068 | 5.3442 | 2.0294 | 0.35845 | 1 | 5.4185 | 0.088981 | 66.3762
| 0 | 150 | 20 |  |  |  |  | Operating Conditions | [11 empty] | 6 | 45 | 1.953 | 46366.1321 | 1.9965e+20 | 0.03395 | 0.023204 | 0.23292 | 0.28244 | 0.20968 | 0.66621 | 1.078 | 0.20968 | 0.34874 | 0.13906 | 5.3361 | 2.0213 | 0.35305 | 1 | 5.3967 | 0.13847 | 66.6597
| 20 | 147 | 28 |  |  |  |  | Flowrate |  |  | 108.8206 | US gpm | [7 empty] | 7 | 54 | 2.3435 | 55639.3585 | 2.5233e+20 | 0.0018363 | 0.022534 | 0.32573 | 0.27957 | 0.20788 | 0.66567 | 1.0751 | 0.20788 | 0.34586 | 0.13799 | 5.3307 | 2.0159 | 0.34946 | 1 | 5.3821 | 0.19886 | 66.9985
| 50 | 140 | 37 |  |  |  |  | Head |  |  | 115.3477 | ft | [7 empty] | 8 | 63 | 2.7341 | 64912.5849 | 3.0381e+20 | 0.00015588 | 0.022017 | 0.43318 | 0.27751 | 0.20659 | 0.66528 | 1.0731 | 0.20659 | 0.34381 | 0.13722 | 5.3269 | 2.012 | 0.34689 | 1 | 5.3717 | 0.27015 | 67.3922
| 80 | 129 | 43 |  |  |  |  | Efficiency |  |  | 45.5429 | % | [7 empty] | 9 | 72 | 3.1247 | 74185.8114 | 3.5359e+20 | 1.8404e-05 | 0.021604 | 0.55515 | 0.27597 | 0.20563 | 0.66499 | 1.0715 | 0.20563 | 0.34227 | 0.13664 | 5.324 | 2.0091 | 0.34497 | 1 | 5.3639 | 0.35234 | 67.8403
| 100 | 120 | 45 |  |  |  |  | Hydraulic Power |  |  | 3.1697 | bhp | [7 empty] | 10 | 81 | 3.5153 | 83459.0378 | 4.0141e+20 | 2.7957e-06 | 0.021264 | 0.69156 | 0.27477 | 0.20488 | 0.66477 | 1.0703 | 0.20488 | 0.34107 | 0.13619 | 5.3218 | 2.0069 | 0.34347 | 1 | 5.3578 | 0.44542 | 68.3426
| 150 | 90 | 44 |  |  |  |  | Rated Power |  |  | 6.9599 | bhp | [7 empty] | 11 | 90 | 3.9059 | 92732.2642 | 4.4715e+20 | 5.1804e-07 | 0.020979 | 0.84234 | 0.27382 | 0.20428 | 0.66459 | 1.0694 | 0.20428 | 0.34011 | 0.13583 | 5.32 | 2.0051 | 0.34227 | 1 | 5.353 | 0.54941 | 68.8989
| 180 | 67 | 40 | [16 empty] | 12 | 99 | 4.2965 | 102005.4906 | 4.9082e+20 | 1.1274e-07 | 0.020736 | 1.0074 | 0.27303 | 0.20379 | 0.66444 | 1.0686 | 0.20379 | 0.33933 | 0.13554 | 5.3185 | 2.0036 | 0.34129 | 1 | 5.349 | 0.66429 | 69.5091
| 200 | 50 | 35 | [16 empty] | 13 | 108 | 4.6871 | 111278.7171 | 5.3245e+20 | 2.802e-08 | 0.020526 | 1.1868 | 0.27238 | 0.20339 | 0.66432 | 1.0679 | 0.20339 | 0.33868 | 0.13529 | 5.3173 | 2.0024 | 0.34047 | 1 | 5.3457 | 0.79007 | 70.1729
[20 empty] | 14 | 117 | 5.0777 | 120551.9435 | 5.7211e+20 | 7.7852e-09 | 0.020343 | 1.3804 | 0.27183 | 0.20304 | 0.66422 | 1.0674 | 0.20304 | 0.33812 | 0.13508 | 5.3162 | 2.0014 | 0.33978 | 1 | 5.3429 | 0.92675 | 70.8904
[20 empty] | 15 | 126 | 5.4683 | 129825.1699 | 6.0989e+20 | 2.3786e-09 | 0.020181 | 1.5882 | 0.27135 | 0.20274 | 0.66413 | 1.0669 | 0.20274 | 0.33765 | 0.13491 | 5.3153 | 2.0005 | 0.33919 | 1 | 5.3405 | 1.0743 | 71.6613
[20 empty] | 16 | 135 | 5.8589 | 139098.3963 | 6.4588e+20 | 7.8868e-10 | 0.020036 | 1.8101 | 0.27094 | 0.20249 | 0.66405 | 1.0665 | 0.20249 | 0.33724 | 0.13475 | 5.3146 | 1.9997 | 0.33868 | 1 | 5.3384 | 1.2328 | 72.4857
[20 empty] | 17 | 144 | 6.2494 | 148371.6227 | 6.8019e+20 | 2.8083e-10 | 0.019907 | 2.0462 | 0.27058 | 0.20226 | 0.66398 | 1.0661 | 0.20226 | 0.33688 | 0.13462 | 5.3139 | 1.999 | 0.33823 | 1 | 5.3366 | 1.4022 | 73.3634
[20 empty] | 18 | 153 | 6.64 | 157644.8492 | 7.1291e+20 | 1.0646e-10 | 0.019791 | 2.2965 | 0.27026 | 0.20206 | 0.66392 | 1.0658 | 0.20206 | 0.33656 | 0.1345 | 5.3133 | 1.9984 | 0.33783 | 1 | 5.335 | 1.5824 | 74.2944
[20 empty] | 19 | 162 | 7.0306 | 166918.0756 | 7.4413e+20 | 4.2658e-11 | 0.019685 | 2.5608 | 0.26998 | 0.20189 | 0.66387 | 1.0655 | 0.20189 | 0.33628 | 0.13439 | 5.3128 | 1.9979 | 0.33748 | 1 | 5.3336 | 1.7736 | 75.2787
[20 empty] | 20 | 171 | 7.4212 | 176191.302 | 7.7394e+20 | 1.796e-11 | 0.019589 | 2.8393 | 0.26973 | 0.20173 | 0.66382 | 1.0653 | 0.20173 | 0.33603 | 0.1343 | 5.3123 | 1.9974 | 0.33716 | 1 | 5.3323 | 1.9757 | 76.3161
[20 empty] | 21 | 180 | 7.8118 | 185464.5284 | 8.0243e+20 | 7.9047e-12 | 0.0195 | 3.1319 | 0.2695 | 0.20159 | 0.66378 | 1.0651 | 0.20159 | 0.3358 | 0.13421 | 5.3119 | 1.997 | 0.33688 | 1 | 5.3312 | 2.1887 | 77.4068
Piping Inside Diameter, Inches
| Sch / Thickness |  |  | Nominal Pipe Size | 0.375 | 0.5 | 1 | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | OD
1 | 0.375 | 1 | 1 | 0.5 | [6 empty] | 0.622 |  | 0.546 |  |  |  | 0.466 | 0.84 | 1
2 | 0.5 | 2 | 2 | 0.75 | [6 empty] | 0.824 |  | 0.742 |  |  |  | 0.612 | 1.05 | 2
3 | 1 | 3 | 3 | 1 | 0.565 | [5 empty] | 1.049 |  | 0.957 |  |  |  | 0.815 | 1.315 | 3
4 | 10 | 4 | 4 | 1.5 | 1.15 | [5 empty] | 1.61 |  | 1.5 |  |  |  | 1.338 | 1.9 | 4
5 | 20 | 5 | 5 | 2 | 1.625 | [5 empty] | 2.067 |  | 1.939 |  |  |  | 1.687 | 2.375 | 5
6 | 30 | 6 | 6 | 3 | 2.75 | [5 empty] | 3.068 |  | 2.9 |  |  |  | 2.624 | 3.5 | 6
7 | 40 | 7 | 7 | 4 | 3.75 | [5 empty] | 4.026 |  | 3.826 |  | 3.624 |  | 3.438 | 4.5 | 7
8 | 60 | 8 | 8 | 6 | 5.875 | [5 empty] | 6.065 |  | 5.761 |  | 5.501 |  | 5.187 | 6.625 | 8
9 | 80 | 9 | 9 | 8 | 7.875 | 7.625 |  |  | 8.125 | 8.071 | 7.981 | 7.813 | 7.625 | 7.437 | 7.187 | 7.001 | 6.8713 | 8.625 | 9
10 | 100 | 10 | 10 | 10 | 10 | 9.75 |  |  | 10.25 | 10.136 | 10.02 | 9.75 | 9.562 | 9.312 | 9.062 | 8.75 | 8.5 | 10.75 | 10
11 | 120 | 11 | 11 | 12 | 12 | 11.75 |  |  | 12.25 | 12.06 | 11.938 | 11.626 | 11.374 | 11.062 | 10.75 | 10.5 | 10.126 | 12.75 | 11
12 | 140 | 12 | 12 | 14 | 13.25 | 13 |  | 13.5 | 13.376 | 13.25 | 13.124 | 12.812 | 12.5 | 12.124 | 11.812 | 11.5 | 11.188 | 14 | 12
13 | 160 | 13 | 13 | 16 | 15.25 | 15 |  | 15.5 | 15.376 | 15.25 | 15 | 14.688 | 14.312 | 13.938 | 13.562 | 13.124 | 12.812 | 16 | 13
|  |  | 14 | 18 | 17.25 | 17 |  | 17.5 | 17.376 | 17.124 | 16.876 | 16.5 | 16.124 | 15.688 | 15.25 | 14.876 | 14.438 | 18 | 14
|  |  | 15 | 20 | 19.25 | 19 |  | 19.5 | 19.25 | 19 | 18.812 | 18.376 | 17.938 | 17.438 | 17 | 16.5 | 16.062 | 20 | 15
|  |  | 16 | 24 | 23.25 | 23 |  | 23.5 | 23.25 | 22.876 | 22.624 | 22.062 | 21.562 | 20.938 | 20.376 | 19.876 | 19.312 | 24 | 16
|  |  | 17 | 26 | 25.25 | 25 |  | 25.376 | 25 | [8 empty] | 26 | 17
|  |  | 18 | 28 | 27.25 | 27 |  | 27.376 | 27 | 26.75 | [7 empty] | 28 | 18
|  |  | 19 | 30 | 29.25 | 29 |  | 29.376 | 29 | 28.75 | [7 empty] | 30 | 19
|  |  | 20 | 32 | 31.25 | 31 |  | 31.376 | 31 | 30.75 | 30.624 | [6 empty] | 32 | 20
|  |  | 21 | 34 | 33.25 | 33 |  | 33.312 | 33 | 32.75 | 32.624 | [6 empty] | 34 | 21
|  |  | 22 | 36 | 35.25 | 35 |  | 35.376 | 35 | 34.75 | 34.5 | [6 empty] | 36 | 22
|  |  | 23 | 38 | 37.25 | 37 | [11 empty] | 38 | 23
|  |  | 24 | 40 | 39.25 | 39 | [11 empty] | 40 | 24
|  |  | 25 | 42 | 41.25 | 41 | [11 empty] | 42 | 25
|  |  | 26 | 44 | 43.25 | 43 | [11 empty] | 44 | 26
|  |  | 27 | 46 | 45.25 | 45 | [11 empty] | 46 | 27
|  |  | 28 | 48 | 47.25 | 47 | [11 empty] | 48 | 28
|  |  | 29 | 50 | 49.25 | 49 | [11 empty] | 50 | 29
|  |  | 30 | 52 | 51.25 | 51 | [11 empty] | 52 | 30
|  |  | 31 | 54 | 53.25 | 53 | [11 empty] | 54 | 31
|  |  | 32 | 56 | 55.25 | 55 | [11 empty] | 56 | 32
|  |  | 33 | 58 | 57.25 | 57 | [11 empty] | 58 | 33
|  |  | 34 | 60 | 59.25 | 59 | 58 | [10 empty] | 60 | 34
|  |  | 35 | 66 | 65.25 | 65 | 64 | [10 empty] | 66 | 35
|  |  | 36 | 72 | 71.25 | 71 | 70 | [10 empty] | 72 | 36
|  |  | 37 | 78 | 77.25 | 77 | 76 | [10 empty] | 78 | 37
|  |  | 38 | 84 | 83.25 | 83 | 82 | [10 empty] | 84 | 38
|  |  | 39 | 90 | 89.25 | 89 | 88 | [10 empty] | 90 | 39
|  |  | 40 | 96 | 95.25 | 95 | 94 | [10 empty] | 96 | 40
|  |  | 41 | 102 | 101.25 | 101 | 100 | [10 empty] | 102 | 41
|  |  | 42 | 108 | 107.25 | 107 | 106 | [10 empty] | 108 | 42
|  |  | 43 | 114 | 113.25 | 113 | 112 | [10 empty] | 114 | 43
|  |  | 44 | 120 | 119.25 | 119 | 118 | [10 empty] | 120 | 44
h1
P1
P2
Pipe Diameter - ID1
Pipe Length - L1
Pipe Diameter - ID2
Pipe Length - L2
h2

## Metric
PUMP SIZING CALCULATION
CheGuide.com | [8 empty] | Tag No. |  | P-101 |  |  |  |  | Suction Calculations |  |  |  | Outlet Calculations |  |  |  |  | Head Equation (2nd Order Curve Fitting)
Chemical Engineer's Guide | [8 empty] | Description |  | Feed Pump | [13 empty] | -0.011792 | -0.13509 | 45.7001
[9 empty] | Date |  | 06-May-2017 |  |  |  |  | Selected ID |  | 6 |  | Selected ID |  | 6 |  |  | 5.2599e-05 | 0.0026636 | 0.025435
User Input | [8 empty] | By |  | CheGuide |  |  |  |  | Selected Schedule |  | 7 |  | Selected Schedule |  | 7 |  |  | 1 | 0.032062 | #N/A
[16 empty] | Pipe ID Selected |  | 3.068 | inch | Pipe ID Selected |  | 3.068 | inch
[18 empty] | 3.068 | inch |  |  | 3.068 | inch |  | Efficiency Equation (2nd Order Curve Fitting)
[16 empty] | Area |  | 0.0047694 | m2 | Area |  | 0.0047694 | m2 |  | -0.033843 | 1.8644 | 20.1368
Flowrate |  |  | 22.7125 | m³/h | [11 empty] | Velocity |  | 1.3228 | m/s | Velocity |  | 1.3228 | m/s |  | 0.00030306 | 0.015346 | 0.14655
Density |  |  | 999.5521 | kg/m³ | [11 empty] | Re |  | 103035.8533 |  | Re |  | 103035.8533 |  |  | 0.99955 | 0.18473 | #N/A
Viscosity |  |  | 1 | cP | [11 empty] | e/D |  | 0.0005867 |  | e/D |  | 0.0005867
Vapor Pressure |  |  | 1.0342 | bar abs | [11 empty] | A |  | 4.9554e+20 |  | A |  | 4.9554e+20 |  |  | System Curve (2nd Order Curve Fitting)
[16 empty] | B |  | 9.5994e-08 |  | B |  | 9.5994e-08 |  |  | 0.027199 | 0.09284 | 8.4384
Differential DP |  |  | 2.4124 | bar | [11 empty] | f |  | 0.020711 |  | f |  | 0.020711 |  |  | 7.0316e-05 | 0.0029775 | 0.026267
Differential Head |  |  | 24.6027 | m | [11 empty] | DP1 |  | 0.23242 | bar/100m | DP |  | 0.23242 | bar/100m |  | 0.99999 | 0.044006 | #N/A
Hydraulic power |  |  | 1.5205 | kw | [11 empty] | Pressure |  | 1.401 | bar | Pressure |  | 3.8134 | bar
NPSH available |  |  | 3.7402 | m | [20 empty] | Solution of System & Head Curve | [5 empty] | Efficiency | 45.8022 | %
[25 empty] | -0.038991 | -0.22793 | 37.2617
Suction Condition | [7 empty] | Discharge Condition | [7 empty] | Curve Fitting |  |  |  |  | Maximum Flow |  | 40.8824
Pressure |  | P1 | 1.7237 | bar abs |  |  |  | Pressure |  | P2 | 2.0684 | bar abs | [8 empty] | Division |  | 20 |  | Determinant |  | 5.8634 | TRUE | 2.4215 |  |  | X | Y
Static Head |  | h1 | 1.524 | m |  |  |  | Static Head |  | h2 | 3.048 | m |  |  |  | Flow | Head | Efficiency |  |  | Increment |  | 2.0441 |  | Roots |  | -33.9742 | 28.1286 |  |  |  | 28.1286 | 0
Equipment DP |  |  | 0.34474 | bar |  |  |  | Equipment DP |  |  | 0 | bar |  |  | 1 | 0 | 45.72 | 20 | [6 empty] | Selected Flow |  | 28.1286 | GPM | Head | 32.5703 | ft | 28.1286 | 32.5703
Misc DP |  |  | 0 | bar |  |  |  | Misc DP |  |  | 0 | bar |  |  | 2 | 4.5425 | 44.8056 | 28 |  |  |  | Suction Pipe
[15 empty] | 3 | 11.3562 | 42.672 | 37 |  |  | Flow | Velocity | Reynold | A | B | f | DP1 | Elb, 90LR | Elb, 45LR | Tees, Thru | Tees, Bran | Ball | Butterfly | Gate | Globe | Check | Plug | Pipe | Sum K | DP | Suct P | Diff P | System Curve | Pump Head | Efficiency %
Piping | [7 empty] | Piping | [6 empty] | 4 | 18.17 | 39.3192 | 43 |  |  | m3/h | m/s | [5 empty] | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | [6 empty] | %
Length |  | L1 | 36.576 | m |  |  |  | Length |  | L2 | 609.6 | m |  |  | 5 | 22.7125 | 36.576 | 45 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5284 | 0.83891 | 8.5554 | 45.7001 | 20.1368
Pipe Diameter |  |  | 3 | inch |  |  |  | Pipe Diameter |  |  | 3 | inch |  |  | 6 | 34.0687 | 27.432 | 44 |  | 2 | 2.0441 | 0.11905 | 9273.2266 | 1.3052e+19 | 5180397235.9534 | 0.032631 | 0.0029661 | 0.35146 | 0.25281 | 0.67915 | 1.147 | 0.25281 | 0.41776 | 0.16495 | 5.4655 | 2.1507 | 0.43932 | 0.51725 | 5.2633 | 0.00037283 | 1.5269 | 0.85871 | 8.7573 | 45.3747 | 23.8064
Sch/ Thick |  |  | 40 |  |  |  |  | Sch/ Thick |  |  | 40 |  |  |  | 7 | 40.8824 | 20.4216 | 40 |  | 3 | 4.0882 | 0.2381 | 18546.4532 | 4.8691e+19 | 79046.5887 | 0.02768 | 0.010064 | 0.30832 | 0.22585 | 0.67106 | 1.1039 | 0.22585 | 0.37462 | 0.14877 | 5.3847 | 2.0698 | 0.3854 | 0.50863 | 5.0363 | 0.001427 | 1.5233 | 0.90635 | 9.2432 | 44.9508 | 27.1932
Pipe ID |  | ID1 | 77.9272 | mm |  |  |  | Pipe ID |  | ID2 | 77.9272 | mm |  |  | 8 | 45.4249 | 15.24 | 35 |  | 4 | 6.1324 | 0.35716 | 27819.6798 | 9.5328e+19 | 120.3436 | 0.02545 | 0.02082 | 0.29395 | 0.21686 | 0.66836 | 1.0895 | 0.21686 | 0.36024 | 0.14338 | 5.3577 | 2.0428 | 0.36743 | 0.50575 | 4.9607 | 0.0031625 | 1.5176 | 0.97879 | 9.9819 | 44.4283 | 30.2972
[15 empty] | 9 | 45.4249 | 15.24 | 35 |  | 5 | 8.1765 | 0.47621 | 37092.9065 | 1.4673e+20 | 1.2062 | 0.024114 | 0.035071 | 0.28676 | 0.21237 | 0.66702 | 1.0823 | 0.21237 | 0.35305 | 0.14068 | 5.3442 | 2.0294 | 0.35845 | 0.50431 | 4.9228 | 0.0055793 | 1.51 | 1.075 | 10.9627 | 43.8072 | 33.1183
Roughness |  |  | 0.04572 | mm |  |  |  | Roughness |  |  | 0.04572 | mm |  |  | 10 | 45.4249 | 15.24 | 35 |  | 6 | 10.2206 | 0.59526 | 46366.1331 | 1.9965e+20 | 0.03395 | 0.023204 | 0.05273 | 0.28244 | 0.20968 | 0.66621 | 1.078 | 0.20968 | 0.34874 | 0.13906 | 5.3361 | 2.0213 | 0.35305 | 0.50345 | 4.9001 | 0.0086775 | 1.5004 | 1.1943 | 12.1797 | 43.0877 | 35.6567
[20 empty] | 7 | 12.2647 | 0.71431 | 55639.3597 | 2.5233e+20 | 0.0018363 | 0.022534 | 0.07374 | 0.27957 | 0.20788 | 0.66567 | 1.0751 | 0.20788 | 0.34586 | 0.13799 | 5.3307 | 2.0159 | 0.34946 | 0.50288 | 4.885 | 0.012457 | 1.489 | 1.3364 | 13.6294 | 42.2695 | 37.9122
Fittings |  |  | No. | K | DP |  |  | Fittings |  |  | No. | K | DP | [6 empty] | 8 | 14.3089 | 0.83336 | 64912.5863 | 3.0381e+20 | 0.00015588 | 0.022017 | 0.098066 | 0.27751 | 0.20659 | 0.66528 | 1.0731 | 0.20659 | 0.34381 | 0.13722 | 5.3269 | 2.012 | 0.34689 | 0.50246 | 4.8742 | 0.016918 | 1.4756 | 1.5012 | 15.3093 | 41.3529 | 39.8849
Elbows, 90LR |  |  | 1 | 0.27295 | 0.002387 |  |  | Elbows, 90LR |  |  | 1 | 0.27295 | 0.002387 | [6 empty] | 9 | 16.353 | 0.95242 | 74185.8129 | 3.5359e+20 | 1.8404e-05 | 0.021604 | 0.12568 | 0.27597 | 0.20563 | 0.66499 | 1.0715 | 0.20563 | 0.34227 | 0.13664 | 5.324 | 2.0091 | 0.34497 | 0.50216 | 4.8661 | 0.02206 | 1.4604 | 1.6883 | 17.2177 | 40.3377 | 41.5748
Elbows, 45LR |  |  | 1 | 0.20374 | 0.0017818 |  |  | Elbows, 45LR |  |  | 1 | 0.20374 | 0.0017818 | [6 empty] | 10 | 18.3971 | 1.0715 | 83459.0395 | 4.0141e+20 | 2.7957e-06 | 0.021264 | 0.15656 | 0.27477 | 0.20488 | 0.66477 | 1.0703 | 0.20488 | 0.34107 | 0.13619 | 5.3218 | 2.0069 | 0.34347 | 0.50192 | 4.8598 | 0.027884 | 1.4432 | 1.8977 | 19.3531 | 39.2239 | 42.9818
Tees, Thru |  |  | 1 | 0.66443 | 0.0058105 |  |  | Tees, Thru |  |  | 1 | 0.66443 | 0.0058105 | [6 empty] | 11 | 20.4412 | 1.1905 | 92732.2661 | 4.4715e+20 | 5.1804e-07 | 0.020979 | 0.1907 | 0.27382 | 0.20428 | 0.66459 | 1.0694 | 0.20428 | 0.34011 | 0.13583 | 5.32 | 2.0051 | 0.34227 | 0.50173 | 4.8547 | 0.034388 | 1.4243 | 2.1292 | 21.7146 | 38.0116 | 44.1061
Tees, Branch |  |  | 1 | 1.0685 | 0.0093443 |  |  | Tees, Branch |  |  | 1 | 1.0685 | 0.0093443 | [6 empty] | 12 | 22.4853 | 1.3096 | 102005.4928 | 4.9082e+20 | 1.1274e-07 | 0.020736 | 0.22807 | 0.27303 | 0.20379 | 0.66444 | 1.0686 | 0.20379 | 0.33933 | 0.13554 | 5.3185 | 2.0036 | 0.34129 | 0.50157 | 4.8506 | 0.041575 | 1.4034 | 2.3829 | 24.3014 | 36.7008 | 44.9475
Ball Valves |  |  |  | 0.20374 |  |  |  | Ball Valves |  |  |  | 0.20374 | [7 empty] | 13 | 24.5295 | 1.4286 | 111278.7194 | 5.3245e+20 | 2.802e-08 | 0.020526 | 0.26867 | 0.27238 | 0.20339 | 0.66432 | 1.0679 | 0.20339 | 0.33868 | 0.13529 | 5.3173 | 2.0024 | 0.34047 | 0.50144 | 4.8472 | 0.049442 | 1.3807 | 2.6586 | 27.1128 | 35.2914 | 45.506
Butterfly Valves |  |  |  | 0.33925 |  |  |  | Butterfly Valves |  |  |  | 0.33925 | [7 empty] | 14 | 26.5736 | 1.5477 | 120551.946 | 5.7211e+20 | 7.7852e-09 | 0.020343 | 0.3125 | 0.27183 | 0.20304 | 0.66422 | 1.0674 | 0.20304 | 0.33812 | 0.13508 | 5.3162 | 2.0014 | 0.33978 | 0.50133 | 4.8442 | 0.057991 | 1.3561 | 2.9562 | 30.1482 | 33.7835 | 45.7818
Gate Valves |  |  | 1 | 0.13551 | 0.001185 |  |  | Gate Valves |  |  | 1 | 0.13551 | 0.001185 | [6 empty] | 15 | 28.6177 | 1.6667 | 129825.1726 | 6.0989e+20 | 2.3786e-09 | 0.020181 | 0.35954 | 0.27135 | 0.20274 | 0.66413 | 1.0669 | 0.20274 | 0.33765 | 0.13491 | 5.3153 | 2.0005 | 0.33919 | 0.50123 | 4.8418 | 0.067221 | 1.3297 | 3.2758 | 33.4072 | 32.177 | 45.7748
Globe Valves |  |  |  | 5.3183 |  |  |  | Globe Valves |  |  |  | 5.3183 | [7 empty] | 16 | 30.6618 | 1.7858 | 139098.3992 | 6.4588e+20 | 7.8868e-10 | 0.020036 | 0.40979 | 0.27094 | 0.20249 | 0.66405 | 1.0665 | 0.20249 | 0.33724 | 0.13475 | 5.3146 | 1.9997 | 0.33868 | 0.50115 | 4.8396 | 0.077133 | 1.3014 | 3.6172 | 36.8894 | 30.472 | 45.4849
Check Valves |  |  | 1 | 2.0035 | 0.017521 |  |  | Check Valves |  |  |  | 2.0035 | [7 empty] | 17 | 32.706 | 1.9048 | 148371.6258 | 6.8019e+20 | 2.8083e-10 | 0.019907 | 0.46324 | 0.27058 | 0.20226 | 0.66398 | 1.0661 | 0.20226 | 0.33688 | 0.13462 | 5.3139 | 1.999 | 0.33823 | 0.50108 | 4.8377 | 0.087726 | 1.2712 | 3.9805 | 40.5945 | 28.6684 | 44.9122
Plug Valves |  |  |  | 0.34119 |  |  |  | Plug Valves |  |  |  | 0.34119 | [7 empty] | 18 | 34.7501 | 2.0239 | 157644.8524 | 7.1291e+20 | 1.0646e-10 | 0.019791 | 0.5199 | 0.27026 | 0.20206 | 0.66392 | 1.0658 | 0.20206 | 0.33656 | 0.1345 | 5.3133 | 1.9984 | 0.33783 | 0.50101 | 4.836 | 0.099 | 1.2392 | 4.3657 | 44.5222 | 26.7663 | 44.0566
Pipe Entrance |  |  | 1 | 0.50155 | 0.0043861 |  |  | Pipe Exit |  |  | 1 | 1 | 0.0087451 | [6 empty] | 19 | 36.7942 | 2.1429 | 166918.0791 | 7.4413e+20 | 4.2658e-11 | 0.019685 | 0.57975 | 0.26998 | 0.20189 | 0.66387 | 1.0655 | 0.20189 | 0.33628 | 0.13439 | 5.3128 | 1.9979 | 0.33748 | 0.50096 | 4.8345 | 0.11096 | 1.2054 | 4.7726 | 48.6722 | 24.7657 | 42.9183
[5 empty] | 0.042415 | [7 empty] | 0.029254 | [6 empty] | 20 | 38.8383 | 2.262 | 176191.3057 | 7.7394e+20 | 1.796e-11 | 0.019589 | 0.64279 | 0.26973 | 0.20173 | 0.66382 | 1.0653 | 0.20173 | 0.33603 | 0.1343 | 5.3123 | 1.9974 | 0.33716 | 0.50091 | 4.8332 | 0.12359 | 1.1697 | 5.2013 | 53.0444 | 22.6665 | 41.4971
Velocity |  |  | 1.3228 | m/s |  |  |  | Velocity |  |  | 1.3228 | m/s | [7 empty] | 21 | 40.8824 | 2.381 | 185464.5323 | 8.0243e+20 | 7.9047e-12 | 0.0195 | 0.70902 | 0.2695 | 0.20159 | 0.66378 | 1.0651 | 0.20159 | 0.3358 | 0.13421 | 5.3119 | 1.997 | 0.33688 | 0.50086 | 4.832 | 0.13691 | 1.1321 | 5.6518 | 57.6385 | 20.4687 | 39.7931
Reynold's No. |  |  | 103035.8533 |  |  |  |  | Reynold's No. |  |  | 103035.8533
Pipe DP |  |  | 0.23242 | bar/100m |  |  |  | Pipe DP |  |  | 0.23242 | bar/100m | [9 empty] | Discharge Conditions
Suction Pressure |  |  | 1.401 | bar |  |  |  | Discharge Pressure |  |  | 3.8134 | bar | [8 empty] | Flow | Velocity | Reynold | A | B | f | DP1 | Elb, 90LR | Elb, 45LR | Tees, Thru | Tees, Bran | Ball | Butterfly | Gate | Globe | Check | Plug | Pipe | Sum K | DP | Disch P
[21 empty] | GPM | m/s | [5 empty] | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
[20 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2.3673
| Pump Manufacturer's Curve | [6 empty] | Maximum Flow |  |  | 40.8824 | m³/h | [7 empty] | 2 | 2.0441 | 0.11905 | 9273.2266 | 1.3052e+19 | 5180397235.9534 | 0.032631 | 0.0029661 | 0.35146 | 0.25281 | 0.67915 | 1.147 | 0.25281 | 0.41776 | 0.16495 | 5.4655 | 2.1507 | 0.43932 | 1 | 3.5954 | 0.00025468 | 2.3856
[8 empty] | Flow value till which System and Head Curve | [11 empty] | 3 | 4.0882 | 0.2381 | 18546.4532 | 4.8691e+19 | 79046.5887 | 0.02768 | 0.010064 | 0.30832 | 0.22585 | 0.67106 | 1.1039 | 0.22585 | 0.37462 | 0.14877 | 5.3847 | 2.0698 | 0.3854 | 1 | 3.4579 | 0.00097976 | 2.4296
| Flow | Head | Efficiency |  |  |  |  | are calculated | [11 empty] | 4 | 6.1324 | 0.35716 | 27819.6798 | 9.5328e+19 | 120.3436 | 0.02545 | 0.02082 | 0.29395 | 0.21686 | 0.66836 | 1.0895 | 0.21686 | 0.36024 | 0.14338 | 5.3577 | 2.0428 | 0.36743 | 1 | 3.4121 | 0.0021752 | 2.4964
| m³/h | m | % | [16 empty] | 5 | 8.1765 | 0.47621 | 37092.9065 | 1.4673e+20 | 1.2062 | 0.024114 | 0.035071 | 0.28676 | 0.21237 | 0.66702 | 1.0823 | 0.21237 | 0.35305 | 0.14068 | 5.3442 | 2.0294 | 0.35845 | 1 | 3.3892 | 0.0038411 | 2.5849
| 0 | 45.72 | 20 |  |  |  |  | Operating Conditions | [11 empty] | 6 | 10.2206 | 0.59526 | 46366.1331 | 1.9965e+20 | 0.03395 | 0.023204 | 0.05273 | 0.28244 | 0.20968 | 0.66621 | 1.078 | 0.20968 | 0.34874 | 0.13906 | 5.3361 | 2.0213 | 0.35305 | 1 | 3.3754 | 0.0059774 | 2.6947
| 4.5425 | 44.8056 | 28 |  |  |  |  | Flowrate |  |  | 28.1286 | m³/h | [7 empty] | 7 | 12.2647 | 0.71431 | 55639.3597 | 2.5233e+20 | 0.0018363 | 0.022534 | 0.07374 | 0.27957 | 0.20788 | 0.66567 | 1.0751 | 0.20788 | 0.34586 | 0.13799 | 5.3307 | 2.0159 | 0.34946 | 1 | 3.3662 | 0.0085841 | 2.8254
| 11.3562 | 42.672 | 37 |  |  |  |  | Head |  |  | 32.5703 | m | [7 empty] | 8 | 14.3089 | 0.83336 | 64912.5863 | 3.0381e+20 | 0.00015588 | 0.022017 | 0.098066 | 0.27751 | 0.20659 | 0.66528 | 1.0731 | 0.20659 | 0.34381 | 0.13722 | 5.3269 | 2.012 | 0.34689 | 1 | 3.3597 | 0.011661 | 2.9768
| 18.17 | 39.3192 | 43 |  |  |  |  | Efficiency |  |  | 45.8022 | % | [7 empty] | 9 | 16.353 | 0.95242 | 74185.8129 | 3.5359e+20 | 1.8404e-05 | 0.021604 | 0.12568 | 0.27597 | 0.20563 | 0.66499 | 1.0715 | 0.20563 | 0.34227 | 0.13664 | 5.324 | 2.0091 | 0.34497 | 1 | 3.3548 | 0.015209 | 3.1487
| 22.7125 | 36.576 | 45 |  |  |  |  | Hydraulic Power |  |  | 2.4954 | kW | [7 empty] | 10 | 18.3971 | 1.0715 | 83459.0395 | 4.0141e+20 | 2.7957e-06 | 0.021264 | 0.15656 | 0.27477 | 0.20488 | 0.66477 | 1.0703 | 0.20488 | 0.34107 | 0.13619 | 5.3218 | 2.0069 | 0.34347 | 1 | 3.351 | 0.019227 | 3.3409
| 34.0687 | 27.432 | 44 |  |  |  |  | Rated Power |  |  | 5.4482 | kW | [7 empty] | 11 | 20.4412 | 1.1905 | 92732.2661 | 4.4715e+20 | 5.1804e-07 | 0.020979 | 0.1907 | 0.27382 | 0.20428 | 0.66459 | 1.0694 | 0.20428 | 0.34011 | 0.13583 | 5.32 | 2.0051 | 0.34227 | 1 | 3.3479 | 0.023715 | 3.5535
| 40.8824 | 20.4216 | 40 | [16 empty] | 12 | 22.4853 | 1.3096 | 102005.4928 | 4.9082e+20 | 1.1274e-07 | 0.020736 | 0.22807 | 0.27303 | 0.20379 | 0.66444 | 1.0686 | 0.20379 | 0.33933 | 0.13554 | 5.3185 | 2.0036 | 0.34129 | 1 | 3.3454 | 0.028674 | 3.7863
| 45.4249 | 15.24 | 35 | [16 empty] | 13 | 24.5295 | 1.4286 | 111278.7194 | 5.3245e+20 | 2.802e-08 | 0.020526 | 0.26867 | 0.27238 | 0.20339 | 0.66432 | 1.0679 | 0.20339 | 0.33868 | 0.13529 | 5.3173 | 2.0024 | 0.34047 | 1 | 3.3433 | 0.034103 | 4.0392
[20 empty] | 14 | 26.5736 | 1.5477 | 120551.946 | 5.7211e+20 | 7.7852e-09 | 0.020343 | 0.3125 | 0.27183 | 0.20304 | 0.66422 | 1.0674 | 0.20304 | 0.33812 | 0.13508 | 5.3162 | 2.0014 | 0.33978 | 1 | 3.3416 | 0.040002 | 4.3123
[20 empty] | 15 | 28.6177 | 1.6667 | 129825.1726 | 6.0989e+20 | 2.3786e-09 | 0.020181 | 0.35954 | 0.27135 | 0.20274 | 0.66413 | 1.0669 | 0.20274 | 0.33765 | 0.13491 | 5.3153 | 2.0005 | 0.33919 | 1 | 3.34 | 0.046372 | 4.6054
[20 empty] | 16 | 30.6618 | 1.7858 | 139098.3992 | 6.4588e+20 | 7.8868e-10 | 0.020036 | 0.40979 | 0.27094 | 0.20249 | 0.66405 | 1.0665 | 0.20249 | 0.33724 | 0.13475 | 5.3146 | 1.9997 | 0.33868 | 1 | 3.3387 | 0.053212 | 4.9186
[20 empty] | 17 | 32.706 | 1.9048 | 148371.6258 | 6.8019e+20 | 2.8083e-10 | 0.019907 | 0.46324 | 0.27058 | 0.20226 | 0.66398 | 1.0661 | 0.20226 | 0.33688 | 0.13462 | 5.3139 | 1.999 | 0.33823 | 1 | 3.3376 | 0.060523 | 5.2518
[20 empty] | 18 | 34.7501 | 2.0239 | 157644.8524 | 7.1291e+20 | 1.0646e-10 | 0.019791 | 0.5199 | 0.27026 | 0.20206 | 0.66392 | 1.0658 | 0.20206 | 0.33656 | 0.1345 | 5.3133 | 1.9984 | 0.33783 | 1 | 3.3366 | 0.068304 | 5.6049
[20 empty] | 19 | 36.7942 | 2.1429 | 166918.0791 | 7.4413e+20 | 4.2658e-11 | 0.019685 | 0.57975 | 0.26998 | 0.20189 | 0.66387 | 1.0655 | 0.20189 | 0.33628 | 0.13439 | 5.3128 | 1.9979 | 0.33748 | 1 | 3.3357 | 0.076556 | 5.978
[20 empty] | 20 | 38.8383 | 2.262 | 176191.3057 | 7.7394e+20 | 1.796e-11 | 0.019589 | 0.64279 | 0.26973 | 0.20173 | 0.66382 | 1.0653 | 0.20173 | 0.33603 | 0.1343 | 5.3123 | 1.9974 | 0.33716 | 1 | 3.3349 | 0.085278 | 6.371
[20 empty] | 21 | 40.8824 | 2.381 | 185464.5323 | 8.0243e+20 | 7.9047e-12 | 0.0195 | 0.70902 | 0.2695 | 0.20159 | 0.66378 | 1.0651 | 0.20159 | 0.3358 | 0.13421 | 5.3119 | 1.997 | 0.33688 | 1 | 3.3342 | 0.09447 | 6.784
Piping Inside Diameter, Inches
| Sch / Thickness |  |  | Nominal Pipe Size | 0.375 | 0.5 | 1 | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | OD
1 | 0.375 | 1 | 1 | 0.5 | [6 empty] | 0.622 |  | 0.546 |  |  |  | 0.466 | 0.84 | 1
2 | 0.5 | 2 | 2 | 0.75 | [6 empty] | 0.824 |  | 0.742 |  |  |  | 0.612 | 1.05 | 2
3 | 1 | 3 | 3 | 1 | 0.565 | [5 empty] | 1.049 |  | 0.957 |  |  |  | 0.815 | 1.315 | 3
4 | 10 | 4 | 4 | 1.5 | 1.15 | [5 empty] | 1.61 |  | 1.5 |  |  |  | 1.338 | 1.9 | 4
5 | 20 | 5 | 5 | 2 | 1.625 | [5 empty] | 2.067 |  | 1.939 |  |  |  | 1.687 | 2.375 | 5
6 | 30 | 6 | 6 | 3 | 2.75 | [5 empty] | 3.068 |  | 2.9 |  |  |  | 2.624 | 3.5 | 6
7 | 40 | 7 | 7 | 4 | 3.75 | [5 empty] | 4.026 |  | 3.826 |  | 3.624 |  | 3.438 | 4.5 | 7
8 | 60 | 8 | 8 | 6 | 5.875 | [5 empty] | 6.065 |  | 5.761 |  | 5.501 |  | 5.187 | 6.625 | 8
9 | 80 | 9 | 9 | 8 | 7.875 | 7.625 |  |  | 8.125 | 8.071 | 7.981 | 7.813 | 7.625 | 7.437 | 7.187 | 7.001 | 6.8713 | 8.625 | 9
10 | 100 | 10 | 10 | 10 | 10 | 9.75 |  |  | 10.25 | 10.136 | 10.02 | 9.75 | 9.562 | 9.312 | 9.062 | 8.75 | 8.5 | 10.75 | 10
11 | 120 | 11 | 11 | 12 | 12 | 11.75 |  |  | 12.25 | 12.06 | 11.938 | 11.626 | 11.374 | 11.062 | 10.75 | 10.5 | 10.126 | 12.75 | 11
12 | 140 | 12 | 12 | 14 | 13.25 | 13 |  | 13.5 | 13.376 | 13.25 | 13.124 | 12.812 | 12.5 | 12.124 | 11.812 | 11.5 | 11.188 | 14 | 12
13 | 160 | 13 | 13 | 16 | 15.25 | 15 |  | 15.5 | 15.376 | 15.25 | 15 | 14.688 | 14.312 | 13.938 | 13.562 | 13.124 | 12.812 | 16 | 13
|  |  | 14 | 18 | 17.25 | 17 |  | 17.5 | 17.376 | 17.124 | 16.876 | 16.5 | 16.124 | 15.688 | 15.25 | 14.876 | 14.438 | 18 | 14
|  |  | 15 | 20 | 19.25 | 19 |  | 19.5 | 19.25 | 19 | 18.812 | 18.376 | 17.938 | 17.438 | 17 | 16.5 | 16.062 | 20 | 15
|  |  | 16 | 24 | 23.25 | 23 |  | 23.5 | 23.25 | 22.876 | 22.624 | 22.062 | 21.562 | 20.938 | 20.376 | 19.876 | 19.312 | 24 | 16
|  |  | 17 | 26 | 25.25 | 25 |  | 25.376 | 25 | [8 empty] | 26 | 17
|  |  | 18 | 28 | 27.25 | 27 |  | 27.376 | 27 | 26.75 | [7 empty] | 28 | 18
|  |  | 19 | 30 | 29.25 | 29 |  | 29.376 | 29 | 28.75 | [7 empty] | 30 | 19
|  |  | 20 | 32 | 31.25 | 31 |  | 31.376 | 31 | 30.75 | 30.624 | [6 empty] | 32 | 20
|  |  | 21 | 34 | 33.25 | 33 |  | 33.312 | 33 | 32.75 | 32.624 | [6 empty] | 34 | 21
|  |  | 22 | 36 | 35.25 | 35 |  | 35.376 | 35 | 34.75 | 34.5 | [6 empty] | 36 | 22
|  |  | 23 | 38 | 37.25 | 37 | [11 empty] | 38 | 23
|  |  | 24 | 40 | 39.25 | 39 | [11 empty] | 40 | 24
|  |  | 25 | 42 | 41.25 | 41 | [11 empty] | 42 | 25
|  |  | 26 | 44 | 43.25 | 43 | [11 empty] | 44 | 26
|  |  | 27 | 46 | 45.25 | 45 | [11 empty] | 46 | 27
|  |  | 28 | 48 | 47.25 | 47 | [11 empty] | 48 | 28
|  |  | 29 | 50 | 49.25 | 49 | [11 empty] | 50 | 29
|  |  | 30 | 52 | 51.25 | 51 | [11 empty] | 52 | 30
|  |  | 31 | 54 | 53.25 | 53 | [11 empty] | 54 | 31
|  |  | 32 | 56 | 55.25 | 55 | [11 empty] | 56 | 32
|  |  | 33 | 58 | 57.25 | 57 | [11 empty] | 58 | 33
|  |  | 34 | 60 | 59.25 | 59 | 58 | [10 empty] | 60 | 34
|  |  | 35 | 66 | 65.25 | 65 | 64 | [10 empty] | 66 | 35
|  |  | 36 | 72 | 71.25 | 71 | 70 | [10 empty] | 72 | 36
|  |  | 37 | 78 | 77.25 | 77 | 76 | [10 empty] | 78 | 37
|  |  | 38 | 84 | 83.25 | 83 | 82 | [10 empty] | 84 | 38
|  |  | 39 | 90 | 89.25 | 89 | 88 | [10 empty] | 90 | 39
|  |  | 40 | 96 | 95.25 | 95 | 94 | [10 empty] | 96 | 40
|  |  | 41 | 102 | 101.25 | 101 | 100 | [10 empty] | 102 | 41
|  |  | 42 | 108 | 107.25 | 107 | 106 | [10 empty] | 108 | 42
|  |  | 43 | 114 | 113.25 | 113 | 112 | [10 empty] | 114 | 43
|  |  | 44 | 120 | 119.25 | 119 | 118 | [10 empty] | 120 | 44
h1
P1
P2
Pipe Diameter - ID1
Pipe Length - L1
Pipe Diameter - ID2
Pipe Length - L2
h2